|  |  |
| --- | --- |
| BR 023 995 | PremiumLine safety shower valve with draining, wall mounted |
| PremiumLine safety shower valve with draining, wall mounted  - ball valve with lever actuation of stainless steel, DIN-DVGW tested and certificated, water inlet ¾” female  - flow rate at least 60 l/min at 1 bar flow pressure  - lever made of stainless steel, polished, total length 110 mm  - robust ball handle of plastics, black, diameter 30 mm  - actuation via swivel lever, opening angle 90°, not self-closing  - mounting height for lever according to the standards listed below: 0 to 1750 mm height above floor  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 Manufacturer: B-SAFETY or equal Article-No.: BR 023 995  **Technical Specifications**  Minimum flow pressure: 1 bar  Operating pressure: 1 to 5 bar  Flow rate: at least 60 l/min at 1 bar flow pressure  Water inlet: ¾“ female  **Mounting-Instructions**  For an installation in accordance with EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. | |