|  |  |
| --- | --- |
| BR 024 995 | PremiumLine rod operated safety shower valve, ceiling mounted, exposed pipework |
| PremiumLine rod operated safety shower valve, ceiling mounted, exposed pipework- ceiling flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female- ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated- flow rate at least 60 l/min at 1 bar flow pressure- opening angle 90°, not self-closing- pull rod of stainless steel, length 1350 mm, with plastic ball handle, black- holder for pull rod made of stainless steel, polished- information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510- mounting height for lower edge of pull rod handle according to the standards listed below: 0 to 1750 mm height above floor- according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717- according to ANSI Z358.1-2014, DIN EN 15154-1:2006 and DIN EN 15154-5:2019Manufacturer: B-SAFETY or equalArticle-No.: BR 024 995**Technical Specifications**Minimum flow pressure: 1 barOperating pressure: 1 to 5 barFlow rate: at least 60 l/min at 1 bar flow pressureWater inlet: ¾“ female**Mounting-Instructions**For an installation in accordance with DIN EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. |