|  |  |
| --- | --- |
| BR 023 995 | PremiumLine safety shower valve with draining, wall mounted recessed version |
| PremiumLine safety shower valve with draining, wall mounted recessed version - cover plate made of stainless steel, with 4x fixing holes (diameter 4.50 mm) in the corners.- ball valve made of stainless steel, DIN-DVGW tested and approved- including 2x stainless steel union pipe fittings for simplified on-site installation, water inlet ¾” female- flow rate min. 60 litres / minute at 1 bar flow pressure- adjustable plastic clamp-lever-handle, lockable with tools, orange, total length 110 mm- actuation via swivelling lever, opening angle 90°, not self-closing- integrated draining valve for automatic or manual emptying- information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510- mounting height for levers according to the standards mentioned below: 0 to 1750 mm height above floor level- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019Manufacturer: B-SAFETY or equalArticle-No.: BR 027 995**Technical Specifications**Minimum flow pressure: 1 barOperating pressure: 1 to 5 barFlow rate: at least 60 l/min at 1 bar flow pressureWater inlet: ¾“ female**Mounting-Instructions**For an installation in accordance with EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. |