|  |  |
| --- | --- |
| BR 028 995 | PremiumLine safety shower valve in stainless steel cabinet, with draining, wall mounted, recessed version |
| PremiumLine safety shower valve in stainless steel cabinet, with draining, wall mounted, recessed version- recessed stainless steel cabinet, cover for maintenance work removable, dimensions (H x W): 400 x 270 mm, installation dimensions (H x W x D): 350 x 220 x 60 mm- ball valve ¾“ of stainless steel, with lever actuation, DIN-DVGW tested and certificated, water inlet ¾” female- flow rate at least 60 l/min at 1 bar flow pressure- opening angle 90°, not self-closing- lever made of stainless steel, polished, length 160 mm- robust handle of plastics, black, diameter 25 mm, length 90 mm- integrated drain valve with automatic or manual drain, mounted on the outside of the lid- mounting height for lever according to the standards listed below: 0 to 1750 mm height above floor- according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717- according to ANSI Z358.1-2014, DIN EN 15154-1:2006 and DIN EN 15154-5:2019Manufacturer: B-SAFETY or equalArticle-No.: BR 028 995**Technical Specifications**Minimum flow pressure: 1 barOperating pressure: 1 to 5 barFlow rate: at least 60 l/min at 1 bar flow pressureWater inlet: ¾“ female**Mounting-Instructions**For an installation in accordance with DIN EN 15154-1:2006 it must be ensured, that the safety shower installation is self-draining between valve and shower head. |