|  |  |
| --- | --- |
| BR 084 185 / V | ClassicLine variable body safety shower, above door installation, exposed pipework |
| ClassicLine variable body safety shower, above door installation, exposed pipework- ball valve made of dezincification-resistant brass with pull rod actuation on wall flange, of stainless steel can be mounted either on the right or left side of the door, DIN-DVGW tested and certificated, water inlet ¾” female- pull rod with ring handle of stainless steel, chemical resistant green powder coated, length variable (min. 955 mm - max. 1660 mm)- holder for pull rod made of steel, chemical resistant green powder coated- connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length variable according to specification (total width min. 285 mm - max. 1535 mm)- wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated- wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 525 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- coupling sleeve ¾“ of stainless steel, chemical resistant green powder coated- connection pipe ¾“ of stainless steel, chemical resistant green powder coated, headroom variable according to specification (min. 395 mm - max. 1100 mm)- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- mounting height according to the standards listed below: lower edge of high-performance shower head 2200 mm (± 100 mm) height above floor level- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 084 185 / V**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate: 50 l/minWater inlet: ¾“ female**Product overview****BR 084 185 / V:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 084 185 / V75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 084 185 / V110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |