|  |  |
| --- | --- |
| BR 084 185 / V | ClassicLine variable body safety shower, above door installation, exposed pipework |
| ClassicLine variable body safety shower, above door installation, exposed pipework  - ball valve made of dezincification-resistant brass with pull rod actuation on wall flange, of stainless steel can be mounted either on the right or left side of the door, DIN-DVGW tested and certificated, water inlet ¾” female  - pull rod with ring handle of stainless steel, chemical resistant green powder coated, length variable (min. 955 mm - max. 1660 mm)  - holder for pull rod made of steel, chemical resistant green powder coated  - connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length variable according to specification (total width min. 285 mm - max. 1535 mm)  - wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated  - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 525 mm  - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - coupling sleeve ¾“ of stainless steel, chemical resistant green powder coated  - connection pipe ¾“ of stainless steel, chemical resistant green powder coated, headroom variable according to specification (min. 395 mm - max. 1100 mm)  - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - mounting height according to the standards listed below: lower edge of high-performance shower head 2200 mm (± 100 mm) height above floor level  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 084 185 / V  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate: 50 l/min  Water inlet: ¾“ female  **Product overview**  **BR 084 185 / V:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 084 185 / V75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 084 185 / V110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |