|  |  |
| --- | --- |
| BR 085 095 | PremiumLine body safety shower, ceiling mounted, exposed pipework |
| PremiumLine body safety shower, ceiling mounted, exposed pipework- ceiling flange 3-fold of stainless steel with 2 connections for integration into a circulation pipe, mounting plate made of stainless steel with 4 mounting holes, polished, water inlet ¾” female- plug 3/4“ with stainless steel- ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated- pull rod with ring handle of steel, polished, length 700 mm- ceiling shower arm ¾“ of stainless steel, polished, headroom 270 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- mounting height 2445 mm (± 100 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 085 095**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate: 50 l/minWater inlet: ¾“ femaleDimensions (H x W x D): 700 x 172 x 86 mm**Product overview****BR 085 095:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 085 095 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 085 095 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |