|  |  |
| --- | --- |
| BR 088 085 / V | ClassicLine variable body safety shower with pull rod diversion, above door installation, exposed pipework |
| ClassicLine variable body safety shower with pull rod diversion, above door installation, exposed pipework- wall flange 3-fold of stainless steel with 2 connections for integration into a circulation pipe, mounting plate made of stainless steel with 4 mounting holes, chemical-resistant green powder-coated, water inlet ¾” female- plug 3/4“ with stainless steel- screw connection 3/4" of stainless steel, conical sealing, for simplified installation on site- ball valve of stainless steel, DIN-DVGW tested and certificated, with pull rod angle-diversion and wall bracket, length variable according to specification (total width min. 205 mm - max. 1500 mm), can be mounted either on the right or left side of the door- pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm- holder for pull rod made of steel, chemical resistant green powder coated- wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 670 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- mounting height 2345 mm (± 100 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-2:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 088 085 / V**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate: 50 l/minWater inlet: ¾“ femaleDimensions (H x W x D): 790 x 290 - 1585 x 670 mm**Product overview****BR 088 085 / V:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 088 085 / V75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 088 085 / V110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |