|  |  |
| --- | --- |
| BR 200 085 | ClassicLine safety eye shower with two spray heads 45°, table mounted |
| ClassicLine safety eye shower with two spray heads 45°, table mounted - Connection thread 1/2" male, length 60 mm, incl. fastening-parts kit with nut G1/2" with 2 screws M5 for difficult to access mounting, with distribution disc, rosette, sealing to table surface with O-Ring  - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure  - ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated  - big push plate made of steel, chemical resistant green powder coated, length 130 mm, with large signal "PUSH", luminescent according to DIN 67510  - double nipple ½” of stainless steel  - high-performance spray heads for large-scale dispersion of water, 45° angled, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - height 175 mm, total width incl. lever 250 mm  - mounting height 825 mm (± 200 mm)  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014 and EN 15154-2:2006  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 200 085  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 5 bar  Flow rate: 14 l/min  Water inlet: ½“ male | |