|  |  |
| --- | --- |
| BR 305 095 | PremiumLine safety eye shower with stainless steel bowl, floor mounted |
| PremiumLine safety eye shower with stainless steel bowl, floor mounted  - base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm  - stand pipe 1 ¼” of stainless steel, polished, with top and bottom water inlet 1 ¼” female, total height 1040 mm  - connection pipe of stainless steel for easy installation and alignment of the shower, polished  - ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated  - big push plate made of stainless steel, polished, length 240 mm, with large signal "PUSH", luminescent according to DIN 67510 - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure  - high-performance spray heads made of stainless for large-scale dispersion of water, polished, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork - bowl made of stainless steel, diameter 275 mm, polished, water outlet 1 ¼” male  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - total height 1040 mm, projection 380 mm, total width incl. lever 350 mm  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014 and EN 15154-2:2006  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 305 095  **Technical Specifications**  Minimum flow pressure: 2.5 bar  Operating pressure: 2.5 to 5 bar  Flow rate: 14 l/min  Water inlet: 1 ¼” female  Water outlet: 1 ¼” male | |