|  |  |
| --- | --- |
| BR 305 095 | PremiumLine safety eye shower with stainless steel bowl, floor mounted |
| PremiumLine safety eye shower with stainless steel bowl, floor mounted- base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm- stand pipe 1 ¼” of stainless steel, polished, with top and bottom water inlet 1 ¼” female, total height 1050 mm- connection pipe of stainless steel for easy installation and alignment of the shower, polished- ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated- push plate made of stainless steel, polished, length 240 mm, with large signal "PUSH", luminescent according to DIN 67510- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure- high-performance spray heads made of stainless for large-scale dispersion of water, polished, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork- bowl made of stainless steel, diameter 275 mm, polished, water outlet 1 ¼” male- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- total height 1050 mm, projection 415 mm, total width incl. lever 410 mm- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014 and EN 15154-2:2006- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 305 095**Technical Specifications**Minimum flow pressure: 2.5 barOperating pressure: 2.5 to 5 barFlow rate: 14 l/minWater inlet: 1 ¼“ femaleWater outlet: 1 ¼“ maleDimensions (H x W x D): 1050 x 410 x 415 mm |