|  |  |
| --- | --- |
| BR 715 035 | ClassicLine hand-held eye shower with two spray heads, diagonal mounted / lab cell mounted |
| ClassicLine hand-held eye shower with two spray heads, diagonal mounted / lab cell mounted  - ergonomically shaped handle with integrated, adjusting activation made of plastics, valve not self-closing  - high-performance spray heads for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps  - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure - integrated backflow preventer to protect the drinking water - stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated - 45° wall bracket, front mounted, incl. 2x large mounting holes, chrome-plated rosette, sealing to table surface with O-Ring  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - mounting height 680 mm (± 200 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014 and EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 715 035  **Technical Specifications**  Minimum flow pressure: 2.5 bar  Operating pressure: 2.5 to 5 bar  Flow rate: 14 l/min  Water inlet: ½“ female  Dimensions (H x W x D): 310 x 145 x 65 mm | |