|  |  |
| --- | --- |
| BR 820 095 | PremiumLine frostprotected heated body safety shower, wall mounted (inside the wall) |
| PremiumLine frostprotected heated body safety shower, wall mounted (inside the wall)- outer casing of the shower made of screwed stainless steel housing, easy to dismantle for maintenance work, including green/white indicator strips for better visibility of the shower, water inlet 1” male- connection adapter of stainless steel, polished- connection pipe ¾” of stainless steel, polished, length 75 mm- ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated- pull rod with ring handle of stainless steel, polished, length 700 mm- wall shower arm ¾“ of stainless steel, polished, projection 755 mm- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining- insulation made of mineral wool shape package, non-flammable, according to DIN 4102- heating by self-regulating trace tape, output 12 W/m, electrical supply 230 V - 50 Hz- outdoor thermostat and power-saving-circuit (shutdown of trace tape at 14°C, switch on at 4°C)- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 meter- mounting height 2345 mm (± 100 mm)- suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 820 095**Technical Specifications**Minimum flow pressure: 1 barOperating pressure: 1 to 5 barFlow rate: 110 l/minWater inlet: 1” maleElectrical supply: 230 V - 50 Hz |