|  |  |
| --- | --- |
| BR 820 095 | PremiumLine frostprotected heated body safety shower, wall mounted (inside the wall) |
| PremiumLine frostprotected heated body safety shower, wall mounted (inside the wall)  - outer casing of the shower made of screwed stainless steel housing, easy to dismantle for maintenance work, including green/white indicator strips for better visibility of the shower, water inlet 1” male  - connection adapter of stainless steel, polished  - connection pipe ¾” of stainless steel, polished, length 75 mm  - ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, polished, length 700 mm  - wall shower arm ¾“ of stainless steel, polished, projection 755 mm  - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining  - insulation made of mineral wool shape package, non-flammable, according to DIN 4102  - heating by self-regulating trace tape, output 12 W/m, electrical supply 230 V - 50 Hz  - outdoor thermostat and power-saving-circuit (shutdown of trace tape at 14°C, switch on at 4°C)  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 meter  - mounting height 2345 mm (± 100 mm)  - suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 820 095  **Technical Specifications**  Minimum flow pressure: 1 bar  Operating pressure: 1 to 5 bar  Flow rate: 110 l/min  Water inlet: 1” male  Electrical supply: 230 V - 50 Hz | |