|  |  |
| --- | --- |
| BR 826 095 | PremiumLine frostprotected heated eye-/face wash unit with bowl and lid, wall mounted, exposed pipework |
| PremiumLine frostprotected heated eye-/face wash unit with bowl and lid, wall mounted, exposed pipework  - housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male  - integrated protective cover against dust  - actuation by pulling down the lid - ball valve 3/8“ of stainless steel, with lever actuation by lid, DIN-DVGW tested and certificated  - aerators made of brass with a very limited spray pattern, chrome-plated  - with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male  - insulation made of mineral wool shape package, non-flammable, according to DIN 4102  - heating by self-regulating trace tape, output 23 W/m, electrical supply 230 V - 50 Hz  - outdoor thermostat and power-saving-circuit (shutdown of trace tape at 14°C, switch on at 4°C)  - inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre  - height 285 mm, width 356 mm, depth 305 mm  - mounting height (lower edge) 910 mm (± 200 mm)  - suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014 and EN 15154-2:2006  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 826 095  **Technical Specifications**  Minimum flow pressure: 2.5 bar  Operating pressure: 2.5 to 5 bar  Flow rate: 14-20 l/min  Water inlet: 3/8” male  Water outlet: 1 ½” male  Electrical supply: 230 V - 50 Hz  Dimensions (H x W x D): 285 x 356 x 305 mm | |