|  |  |
| --- | --- |
| BR 830 095 | PremiumLine body safety shower, floor mounted |
| PremiumLine body safety shower, floor mounted- including top and bottom water inlet 1 ¼” female for installation in circulation lines, plug 1 ¼” of stainless steel- base plate with 4 mounting holes of stainless steel, polished, diameter 200 mm- stand pipe 1 ¼” of stainless steel three-part, polished, with top and bottom water inlet 1 ¼” female, total height 2330 mm- connection piece of stainless steel, for easy installation and alignment of the shower- ball valve ¾” of stainless steel, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, polished, length 700 mm- wall shower arm ¾“ of stainless steel, polished, projection 630 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely free of calcification-and maintenance, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 830 095**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate: 50 l/minWater inlet: 1 ¼” female**Product overview****BR 830 095:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 830 095 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 830 095 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |