|  |  |
| --- | --- |
| BR 837 595 | PremiumLine body safety shower with eye shower with stainless steel bowl, draining of the eye shower over the stand pipe, floor mounted |
| PremiumLine body safety shower with eye shower with stainless steel bowl, draining of the eye shower over the stand pipe, floor mounted  - including top and bottom water inlet 1 ¼” female for installation in circulation lines, plug 1 ¼” of stainless steel  - base plate with 4 mounting holes of stainless steel, polished, diameter 200 mm  - stand pipe 1 ¼” of stainless steel three-part, polished, with top and bottom water inlet 1 ¼” female, total height 2300 mm  - connection piece of stainless steel, for easy installation and alignment of the shower  - ball valve ¾” of stainless steel, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, polished, length 700 mm  - wall shower arm ¾“ of stainless steel, polished, projection 630 mm  - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely free of calcification-and maintenance, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - integrated PremiumLine safety eye shower with stainless steel bowl  - connection pipe of stainless steel for easy installation and alignment of the shower, polished  - ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated  - big push plate made of stainless steel, polished, length 240 mm, with large signal "PUSH", luminescent according to DIN 67510 - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure  - high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork  - bowl made of stainless steel, diameter 275 mm, polished, water outlet 1 ¼” male - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 837 595  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate body shower: 50 l/min  Water inlet: 1 ¼” female  Dimensions: (H x W x D): 2300 x 400 x 630 mm  **Technical specifications eye shower**  Minimum flow pressure: 2.5 bar  Operating pressure: 2.5 to 5 bar  Flow rate: 14 l/min  Water outlet: 1 ¼” male  **Product overview**  **BR 837 595:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 837 595 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 837 595 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |