|  |  |
| --- | --- |
| BR 838 085 | ClassicLine body safety shower with eye-/face wash unit with bowl and lid, floor mounted |
| ClassicLine body safety shower with eye-/face wash unit with bowl and lid, floor mounted  - including top and bottom water inlet 1 ¼” female for installation in circulation lines, plug 1 ¼” of stainless steel  - base plate with 4 mounting holes of stainless steel, chemical resistant green powder coated, diameter 200 mm  - stand pipe 1 ¼” of stainless steel three-part, chemical resistant green powder coated, with top and bottom water inlet 1 ¼” female, total height 2330 mm  - connection piece of stainless steel, for easy installation and alignment of the shower  - ball valve ¾” of brass, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm  - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 630 mm  - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely free of calcification-and maintenance, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - integrated PremiumLine eye-/face wash unit with bowl and lid - housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male  - integrated protective cover against dust  - actuation by pulling down the lid - ball valve 3/8“ of stainless steel, with lever actuation by lid, DIN-DVGW tested and certificated  - aerators made of brass with a very limited spray pattern, chrome-plated  - with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male  - inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 838 085  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate body shower: 50 l/min  Flow rate eye shower: 14 l/min  Water inlet: 1 ¼” female  **Product overview**  **BR 838 085:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 838 085 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 838 085 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |