|  |  |
| --- | --- |
| BR 868 085 | ClassicLine safety shower combination, with eye-/face wash unit with bowl and lid, wall mounted, exposed pipework |
| ClassicLine safety shower combination, with eye-/face wash unit with bowl and lid, wall mounted, exposed pipework- including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel- wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female- connection piece ¾” of stainless steel, for easy installation and alignment of the shower- ball valve ¾” of stainless steel, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated- pull rod with ring handle of steel, chemical resistant green powder coated, length 700 mm- wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 625 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- two connection pipes ¾“ of stainless steel, chemical resistant green powder coated, total length 1500 mm- wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female- integrated PremiumLine eye-/face wash unit with bowl and lid- housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male- integrated protective cover against dust- actuation by pulling down the lid- ball valve 3/8“ of stainless steel, with lever actuation by lid, DIN-DVGW tested and certificated- aerators made of brass with a very limited spray pattern, chrome-plated- with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male- inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre- mounting height 810 mm (± 100 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 868 085**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate body shower: 50 l/minFlow rate eye shower: 14 l/minWater inlet: ¾“ female**Product overview****BR 868 085:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 868 085 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 868 085 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019)  |