|  |  |
| --- | --- |
| BR 871 085 | ClassicLine body safety shower with eye shower, above door installation, exposed pipework |
| C ClassicLine body safety shower with eye shower, above door installation, exposed pipework  - including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel  - wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female  - integrated ClassicLine safety eye shower with two spray heads 45°  - connection pipe of stainless steel for easy installation and alignment of the shower, chemical resistant green powder coated, water inlet ¾” male  - ball valve ½” of made of dezincification-resistant brass, with PUSH-lever actuation, DIN-DVGW tested and certificated  - big push plate made of steel, chemical resistant green powder coated, length 130 mm, with large signal "PUSH", luminescent according to DIN 67510  - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure  - high-performance spray heads for large-scale dispersion of water, 45° angled, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - two connection pipes ¾“ of stainless steel, chemical resistant green powder coated, total length 1500 mm  - wall flange as T-version with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female  - connection adapter of stainless steel, polished, with integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length 75 mm  - ball valve ¾” of brass, with pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm  - holder for pull rod made of steel, chemical resistant green powder coated  - connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length 500 mm  - wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female  - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 525 mm  - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcificartion- and maintenance-free, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - mounting height 810 mm (± 100 mm)  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 871 085  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate body shower: 50 l/min  Water inlet: ¾“ female  Dimensions: (H x W x D): 1625 x 940 x 535 mm  **Technical specifications eye shower**  Minimum flow pressure: 1,5 bar  Operating pressure: 1,5 bis 5 bar  Flow rate: 14 l/min  **Product overview**  **BR 871 085:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 871 085 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 871 085 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |