|  |  |
| --- | --- |
| BR 871 085 | ClassicLine body safety shower with eye shower, above door installation, exposed pipework |
| C ClassicLine body safety shower with eye shower, above door installation, exposed pipework- including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel- wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female- integrated ClassicLine safety eye shower with two spray heads 45°- connection pipe of stainless steel for easy installation and alignment of the shower, chemical resistant green powder coated, water inlet ¾” male- ball valve ½” of made of dezincification-resistant brass, with PUSH-lever actuation, DIN-DVGW tested and certificated- big push plate made of steel, chemical resistant green powder coated, length 130 mm, with large signal "PUSH", luminescent according to DIN 67510- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure- high-performance spray heads for large-scale dispersion of water, 45° angled, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- two connection pipes ¾“ of stainless steel, chemical resistant green powder coated, total length 1500 mm- wall flange as T-version with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female- connection adapter of stainless steel, polished, with integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length 75 mm- ball valve ¾” of brass, with pull rod actuation, DIN-DVGW tested and certificated- pull rod with ring handle of stainless steel, chemical resistant green powder coated, length 700 mm- holder for pull rod made of steel, chemical resistant green powder coated- connection pipe ¾“ of stainless steel, chemical resistant green powder coated, length 500 mm- wall flange with 4 mounting holes of stainless steel, chemical resistant green powder coated, water inlet ¾” female- wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 525 mm- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcificartion- and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- mounting height 810 mm (± 100 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 871 085**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate body shower: 50 l/minWater inlet: ¾“ femaleDimensions: (H x W x D): 1625 x 940 x 535 mm**Technical specifications eye shower**Minimum flow pressure: 1,5 barOperating pressure: 1,5 bis 5 barFlow rate: 14 l/min**Product overview****BR 871 085:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 871 085 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 871 085 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |