|  |  |
| --- | --- |
| BR 873 095 | PremiumLine body safety shower with hand-held eye shower with one spray head 45°, above door installation, exposed pipework |
| PremiumLine body safety shower with hand-held eye shower with one spray head 45°, above door installation, exposed pipework  - including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel  - wall flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female  - inclusive ClassicLine hand-held eye shower with one spray head 45°, wall mounted  - ergonomically shaped handle with integrated, adjusting activation made of plastics, valve not self-closing  - high-performance spray head for large-scale dispersion of water, 45° angled, with plastic spray plate, largely scale-free, with rubber sleeves and sealed dust caps - integrated flow regulation 7 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - integrated backflow preventer to protect the drinking water - stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated  - robust table and wall mounting bracket with positioning of the shower, accessories M28x1,5x80mm, incl. fastening-parts kit with nut M28x1,5mm and 2 screws M5 for mounting difficult to access, sealing to table surface with O-Ring  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - two connection pipes ¾“ of stainless steel, polished, total length 1500 mm  - wall flange as T-version with 4 mounting holes of stainless steel, polished, water inlet ¾” female  - connection adapter of stainless steel, polished, with integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - connection pipe ¾“ of stainless steel, polished, length 75 mm  - ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, polished, length 700 mm  - holder for pull rod made of stainless steel, polished  - connection pipe ¾“ of stainless steel, polished, length 500 mm  - wall flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female  - wall shower arm ¾“ of stainless steel, polished, projection 525 mm  - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - mounting height 810 mm (± 100 mm)  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 873 095  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate body shower: 50 l/min  Flow rate eye shower: 7 l/min  Water inlet: ¾“ female  **Product overview**  **BR 873 095:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 873 095 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 873 095 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |