|  |  |
| --- | --- |
| BR 873 095 | PremiumLine body safety shower with hand-held eye shower with one spray head 45°, above door installation, exposed pipework |
| PremiumLine body safety shower with hand-held eye shower with one spray head 45°, above door installation, exposed pipework- including top and bottom water inlet ¾” female for installation in circulation lines, plug ¾” of stainless steel- wall flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female- inclusive ClassicLine hand-held eye shower with one spray head 45°, wall mounted- ergonomically shaped handle with integrated, adjusting activation made of plastics, valve not self-closing- high-performance spray head for large-scale dispersion of water, 45° angled, with plastic spray plate, largely scale-free, with rubber sleeves and sealed dust caps- integrated flow regulation 7 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure- integrated backflow preventer to protect the drinking water- stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated- robust table and wall mounting bracket with positioning of the shower, accessories M28x1,5x80mm, incl. fastening-parts kit with nut M28x1,5mm and 2 screws M5 for mounting difficult to access, sealing to table surface with O-Ring- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- two connection pipes ¾“ of stainless steel, polished, total length 1500 mm- wall flange as T-version with 4 mounting holes of stainless steel, polished, water inlet ¾” female- connection adapter of stainless steel, polished, with integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- connection pipe ¾“ of stainless steel, polished, length 75 mm- ball valve ¾” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated- pull rod with ring handle of stainless steel, polished, length 700 mm- holder for pull rod made of stainless steel, polished- connection pipe ¾“ of stainless steel, polished, length 500 mm- wall flange with 4 mounting holes of stainless steel, polished, water inlet ¾” female- wall shower arm ¾“ of stainless steel, polished, projection 525 mm- high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely scale and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- mounting height 810 mm (± 100 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 873 095**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate body shower: 50 l/minFlow rate eye shower: 7 l/minWater inlet: ¾“ female**Product overview****BR 873 095:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 873 095 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 873 095 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019)  |