|  |  |
| --- | --- |
| BR 880 095 | PremiumLine frost-protected self-draining eye shower, actuation by 3-way ball valve, wall mounted |
| PremiumLine frost-protected self-draining eye shower, actuation by 3-way ball valve, wall mounted- 3-way-ball-valve ¾” of brass that automatically drains the shower downwards when not in use, water inlet ¾” female- spindle extension, standard length 800 mm, can be shortened to the appropriate length on site, including stainless steel push rosette to cover the installation- adjustable plastic clamp-lever-handle made of die-cast zinc, orange plastic-coated, stainless steel bushing, lockable with tools, orange, total length 110 mm- actuation via swivelling lever, opening angle 90°, not self-closing- connection pipe of stainless steel, polished, length 120 mm, water inlet ¾” female, from behind through the wall- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure- high-performance spray heads for large-scale dispersion of water of stainless steel, polished, 45° angled, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork- push-on rosette of stainless steel to cover the installation- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510- mounting height 900 mm (± 200 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014 and EN 15154-2:2006Manufacturer: B-SAFETY or equalArticle-No.: BR 880 095**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 5 barFlow rate: 14 l/minWater inlet: ¾“ femaleEye-shower dimensions (H x W x D): 120 x 140 x 250 mmSwivelling lever dimensions (H x W x D): 130 x 65 x 95 mm |