|  |  |
| --- | --- |
| BR 885 085 | ClassicLine frost-protected self-draining body safety shower, actuation by 3-way ball valve, wall mounted |
| ClassicLine frost-protected self-draining body safety shower, actuation by 3-way ball valve, wall mounted  - 3-way-ball-valve ¾” of brass that automatically drains the shower downwards when not in use, water inlet ¾” female  - spindle extension, standard length 800 mm, can be shortened to the appropriate length on site  - lever for ball valve  - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - push-on rosette of polyamide to cover the installation  - wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 470 mm  - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - mounting height 2345 mm (± 100 mm)  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019 Manufacturer: B-SAFETY or equal Article-No.: BR 885 085  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate: 50 l/min  Water inlet: ¾“ female  **Product overview**  **BR 885 085:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 885 085 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 885 085 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |