|  |  |
| --- | --- |
| BR 885 085 | ClassicLine frost-protected self-draining body safety shower, actuation by 3-way ball valve, wall mounted |
| ClassicLine frost-protected self-draining body safety shower, actuation by 3-way ball valve, wall mounted- 3-way-ball-valve ¾” of brass that automatically drains the shower downwards when not in use, water inlet ¾” female- spindle extension, standard length 800 mm, can be shortened to the appropriate length on site, including stainless steel push rosette to cover the installation- adjustable plastic clamp-lever-handle, lockable with tools, orange, total length 110 mm- actuation via swivelling lever, opening angle 90°, not self-closing- wall shower arm ¾“ of stainless steel, chemical resistant green powder coated, projection 470 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining- push-on rosette made of plastic, green, to cover the installation - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- information sign "OPEN" for confusion-free use in an emergency, orange, photoluminescent according to DIN 67510- mounting height 2345 mm (± 100 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006 and EN 15154-5:2019Manufacturer: B-SAFETY or equalArticle-No.: BR 885 085**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate: 50 l/minWater inlet: ¾“ femaleWall shower arm dimensions (H x W x D): 175 x 65 x 590 mmSwivelling lever dimensions (H x W x D): 130 x 65 x 95 mm**Product overview****BR 885 085:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 885 085 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 885 085 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |