|  |  |
| --- | --- |
| BR 886 395 | PremiumLine frostprotected self-draining eye shower / safety shower station with surrounding protection cage, with underfloor actuation |
| PremiumLine frostprotected self-draining eye shower / safety shower station with surrounding protection cage, with underfloor actuation- frame made of stainless steel tubes, dimensions (H x W x D): 960 x 850 x 900 mm- platform actuation for eye shower made of galvanized steel, mounted with chain on angle diversion, dimensions (W x D): 800 x 800 mm- angle diversion made of stainless steel, with stainless steel attachment to the standpipe- ball valve made of stainless steel as underfloor actuation, mounted in stainless steel cabinet, with pull rod activation 1000 mm, DIN-DVGW tested and certificated, with automatic self-draining in 1000 mm depth- base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm- stand pipe 1 ¼” of stainless steel two-part, polished, with top and bottom water inlet 1 ¼” female, total height 2330 mm- connection piece ¾” of stainless steel, for easy installation and alignment of the shower- ball valve ¾” of stainless steel, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated - pull rod with ring handle of stainless steel, polished, length 700 mm- wall shower arm ¾“ of stainless steel, polished, projection 625 mm- integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure- high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre - integrated PremiumLine safety eye shower with stainless steel bowl, mounting height 970 mm- connection pipe of stainless steel for easy installation and alignment of the shower, polished- bowl made of stainless steel, diameter 275 mm, polished, water outlet 1 ¼” male- high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 und EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 886 395**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 3 barFlow rate body shower: 50 l/minFlow rate eye shower: 14 l/minWater inlet: ¾” male**Product overview****BR 886 395:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 886 395 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)**BR 886 395 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |