|  |  |
| --- | --- |
| BR 886 395 | PremiumLine frostprotected self-draining eye shower / safety shower station with surrounding protection cage, with underfloor actuation |
| PremiumLine frostprotected self-draining eye shower / safety shower station with surrounding protection cage, with underfloor actuation  - frame made of stainless steel tubes, dimensions (H x W x D): 960 x 850 x 900 mm  - platform actuation for eye shower made of galvanized steel, mounted with chain on angle diversion, dimensions (W x D): 800 x 800 mm  - angle diversion made of stainless steel, with stainless steel attachment to the standpipe  - ball valve made of stainless steel as underfloor actuation, mounted in stainless steel cabinet, with pull rod activation 1000 mm, DIN-DVGW tested and certificated, with automatic self-draining in 1000 mm depth  - base plate with 4 mounting holes of stainless steel, polished, dimensions 200 x 200 mm  - stand pipe 1 ¼” of stainless steel two-part, polished, with top and bottom water inlet 1 ¼” female, total height 2330 mm  - connection piece ¾” of stainless steel, for easy installation and alignment of the shower  - ball valve ¾” of stainless steel, with quick connect system and pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, polished, length 700 mm  - wall shower arm ¾“ of stainless steel, polished, projection 625 mm  - integrated automatic flow regulation 50 l/min. for a spray pattern acc. to the norms at a specified operating range of 1.5 to 3 bar dynamic water pressure  - high-performance shower head of stainless steel, polished, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre  - integrated PremiumLine safety eye shower with stainless steel bowl, mounting height 970 mm  - connection pipe of stainless steel for easy installation and alignment of the shower, polished  - bowl made of stainless steel, diameter 275 mm, polished, water outlet 1 ¼” male  - high-performance spray heads made of stainless steel for large-scale dispersion of water, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps with folding mechanism, mounted over distributor fork  - integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 und EN 15154-5:2019  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 886 395  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 3 bar  Flow rate body shower: 50 l/min  Flow rate eye shower: 14 l/min  Water inlet: ¾” male  **Product overview**  **BR 886 395:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 886 395 / 75L:** flow rate 75 l/min / 20 GPM (hazard class II according to EN 15154-5:2019)  **BR 886 395 / 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |