|  |  |
| --- | --- |
| BR 958 005 | ClassicLine tank eyewash station with stainless steel tank |
| ClassicLine tank eyewash station with stainless steel tank- tank of stainless steel, with a capacity of 16 litres- water inlet via large flap lid on the tank, compressed air connection tyre inflation valve- for mobile use or when no water connection is available- actuation by activation of the hand-held eye shower- hand-held eye shower with one spray head, mounting by wall bracket on the tank- ergonomically shaped handle with integrated, adjusting activation made of plastics, valve not self-closing- aerators made of brass with a very limited spray pattern, chrome-plated - integrated automatic flow regulator 7 litres / minute (1.7 litres / minute / 0.45 GPM) for a standard-compliant spray pattern - integrated backflow preventer- stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated- sign for eye shower according to DIN EN ISO 7010 und ASR A1.3 mounted on the tank, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 metre- dimensions (H x W x D): 560 x 225 x 225 mm- according to ANSI Z358.1-2014Manufacturer: B-SAFETY or equalArticle-No.: BR 958 005**Technical Specifications**Dimensions (H x W): 560 x 225 mmFilling volume: 14 litreFilling pressure: 7 barFlow rates: 7 l/min / 1.7 l/min (0.45 GPM)Flush times: about 2 minutes / 5 minutesWater filling: flap lidCompressed air connection: tyre inflation valve**Product Overview**BR 958 005: flow rate 7 l/min, flush time about 2 minutesBR 958 005 / 1L: flow rate 1.7 l/min (0.45 GPM), flush time about 5 minutes |